| Title | 94. Use and maintenance of eye wash stations in the shop |
| --- | --- |
| Objective | This protocol will help you understand how to use and maintain the eye wash stations in your facility. It will also help you understand what OSHA requirements are for an eye wash station. |
| Responsibility | The manager in charge, Either the SM or the ASM who is currently responsible for the operations of the shop. |
| Steps | - Eyewash stations should be installed at "accessible" locations and reachable within 10 seconds of the hazard. - Both plumbed and self-contained eyewash stations should deliver a 15-minute continuous flow. - Eyewash stations should be installed where caustic or hazardous substances are present. Check all relevant Material Safety Data Sheets at your facility to determine if the chemical or substance requires 15-minute eye flushing. - Eyewash stations should have an on-off valve, door or pull strap that activates within one second with one single motion or less. - The eyewash station should be located in an area free of obstructions that inhibit immediate use. - If your eyewash station has a plastic bowl, it needs to be free of cracks. - The caps on the water nozzles need to be in working order. - If you need to replace either the bowl or caps you can order them from Grainger. - Inform your DM or VP (facilities) of any damaged eyewash stations. - The parts and part numbers are listed below for the Bradley S19-220T eyewash station: Replacement stainless steel bowl: 187-053GR Replacement caps: S05-135 |
| Revision Date | 9/27/23 |